## Slide 1
Basic Design Methods of Heat Exchangers-1
Dr. Yağmur NALBANT ATAK
Atılım University
Department of Mechanical Engineering
ME 453 HEAT EXCHANGER DESIGN 2024-2025 / SPRING

## Slide 2
INTRODUCTION
Basic design methods for two-fluid direct-transfer heat exchangers (recuperators)
Rating problems including
  The heat transfer rate and the fluid outlet temperatures for prescribed fluid flow rates, inlet temperatures, and allowable pressure drop for an existing heat exchanger: hence the heat transfer surface area and the flow passage dimensions are available.
Sizing problems including
  Determination of the dimensions and the size to meet the specified hot and cold fluids inlet and outlet temperatures, flow rates, and pressure drop requirements.

## Slide 3
Basic Equations in Design
General form of the energy balance equation for the Heat Exchangers:
If the change in potential energy of flowing matter is negligible, and drop out.
If heat transfer with surroundings is negligible, drops out.
If the change in kinetic energy of flowing matter is negligible, and drop out.

## Slide 4
Basic Equations in Design
The change of enthalpy of one of the fluid streams:
Heat Transfer Rate
Mass Flow Rate
Specific Enthalpy
Outlet Enthalpy
Inlet Enthalpy
The change of enthalpy of hot and cold fluid streams:
Hot fluid:
Cold fluid:
h: Hot
c: Cold
1: inlet
2: outlet

## Slide 5
Basic Equations in Design
If the fluids do not undergo a phase change and have constant specific heat with;
Hot fluid:
Cold fluid:

## Slide 6
Basic Equations in Design
Cold fluid evaporating at a constant temperature
Hot fluid condensing at a constant temperature

## Slide 7
Overall Heat Transfer Coefficient
The temperature difference between hot and cold fluids () varies with the position in the heat exchanger.
Therefore, in the heat transfer analysis of heat exchangers, it is convenient to establish an appropriate mean value of the temperature difference between hot and cold fluids such that the total heat transfer rate Q between the fluids can be determined from the following equation:
Total hot-side and cold-side heat transfer area (m2)
Average overall heat transfer coefficient (W/m2K)
Mean temperature difference (K)
Total Resistance

## Slide 8
Overall Heat Transfer Coefficient
CONDUCTION:
For plane wall
For tubular wall
Thermal conductivity (W/m-K)
Length (m)

## Slide 9
Overall Heat Transfer Coefficient
CONVECTION:
Heat Transfer Coefficient (W/m2-K)
Surface Area (m2)
Surface Temperature (K)
Fluid Temperature (K)

## Slide 10
Overall Heat Transfer Coefficient
RADIATION:
: Emissivity (0-1)
: Stefan Boltzman Constant (5.67*10-4 (W/m2-K4)
: Surface Area(m2)
: Surface Temperature (K)
: Surrounding Temperature (K)

## Slide 11
Overall Heat Transfer Coefficient
From Energy Conversion:

## Slide 12
Overall Heat Transfer Coefficient
+

## Slide 13
Overall Heat Transfer Coefficient

## Slide 14
Overall Heat Transfer Coefficient
For tubular heat exchangers, we must take into account the conduction resistance in the wall and convection resistances of the fluids at the inner and outer tube surfaces.
Note that:
where inner tube surface:
where outer tube surface:

## Slide 15
FOULING
Heat exchanger surfaces are subject to fouling by fluid impurities, rust formation, or other reactions between the fluid and the wall material. The subsequent deposition of a film or scale on the surface can greatly increase the resistance to heat transfer between fluids.
Additional thermal resistance can be introduced: The Fouling Factor, Rf.
  Depends on operating temperature, fluid velocity, and length of service of the heat exchanger. It is variable during the heat exchanger operation.

## Slide 16
EXTENDED SURFACE (FIN) EFFECTS
Fin reduces the convection heat transfer resistance by increasing surface area.
Expression for overall heat transfer coefficient includes fin efficiency, of the finned surface, which depends on the type of fin.
Subscript «f» fin
Subscript «u» unfinned
Subscript «c» cold stream
Subscript «h» hot stream
or

## Slide 17
EXTENDED SURFACE (FIN) EFFECTS
Total surface area on one side

## Slide 18
EXTENDED SURFACE (FIN) EFFECTS
Overall heat transfer coefficient based on the outside surface area of the wall :
Note that: The overall heat transfer coefficient can be determined from knowledge of the inside and outside heat transfer coefficients, fouling factors, and appropriate geometric parameters.

## Slide 19
Order of Magnitude of Thermal Resistance
For a plane wall of thickness t, and heat transfer coefficients of inside and outside, hi and ho with fouling only on one side:
The order of magnitude and range of h for various conditions are given in Table.

## Slide 20
EXAMPLE
Determine the overall heat transfer coefficient U for liquid-to-liquid heat transfer through 0.003 thick steel plates (k=50 W/m-K) for the following heat transfer coefficients and fouling factors on one side:
Overall Heat Transfer Coefficient: