## Slide 1
Epsilon-NTU METHOD
Dr. Yağmur NALBANT ATAK
Atılım University
Department of Mechanical Engineering
ME 453 HEAT EXCHANGER DESIGN 2024-2025 / SPRING

## Slide 2
INTRODUCTION TO ε-NTU METHOD
The log mean temperature difference (LMTD) method of heat exchanger analysis is simple when the fluid inlet temperatures are known and the outlet temperatures are specified or readily determined from the energy balance expressions. The value of for the exchanger may then be determined.
However, if only the inlet temperatures are known, the use of the LMTD method requires a complex iterative procedure. Therefore, it is preferable to employ an alternative approach termed the effectiveness–NTU (or ε-NTU) method.

## Slide 3
DEFINITIONS FOR ε-NTU METHOD
To define the effectiveness of a heat exchanger, we must first determine the maximum possible heat transfer rate, qmax, for the exchanger. This heat transfer rate could, in principle, be achieved in a counterflow heat exchanger of infinite length.
In such an exchanger, one of the fluids would experience the maximum possible temperature difference,
and Hot and cold fluid heat capacity rates

## Slide 4
DEFINITIONS FOR ε-NTU METHOD
FOR EXAMPLE: Consider a situation for which in which case, from the following equations,
The cold fluid would then experience a larger temperature change and since L∞, it would be heated to the inlet temperature of the hot fluid Accordingly, from the following equation:
and Hot and cold fluid heat capacity rates

## Slide 5
DEFINITIONS FOR ε-NTU METHOD
To calculate maximum possible heat transfer rate ():
If
If
From the foregoing results, we are then prompted to write the general expression

## Slide 6
DEFINITIONS FOR ε-NTU METHOD
It is now logical to define the effectiveness, ε, as the ratio of the actual heat transfer rate for a heat exchanger to the maximum possible heat transfer rate:
Actual heat transfer rate
Maximum possible heat transfer rate
OR
OR
0< <1

## Slide 7
DEFINITIONS FOR ε-NTU METHOD
If the effectiveness (), the inlet temperature of hot stream (), and the inlet temperature of the cold stream () are known, the actual heat transfer rate can be calculates from the following equation:
For any heat exchanger it can be shown that:
where is the capacity rate ratio and equal to or , depending on the relative magnitudes of the hot and cold fluid heat capacity rates.
Number of Transfer Units (NTU) or heat transfer area number is a dimensionless parameter that is widely used for heat exchanger analysis and is defined as:

## Slide 8
Effectiveness-NTU Relations-Parallel Flow
FOR EXAMPLE: Consider a parallel flow heat exchanger for which To determine a specific form of the effectiveness-NTU relation can be found as follows:
OR

## Slide 9
Effectiveness-NTU Relations-Parallel Flow
Now, consider the following equation:
We know the temperature difference for the parallel flow:
When we combined the given equations:

## Slide 10
Effectiveness-NTU Relations-Parallel Flow
When we add and subtract on the left-hand side of the equation:

## Slide 11
Effectiveness-NTU Relations-Parallel Flow
For Parallel Flow
For Counter Flow

## Slide 12
Effectiveness-NTU Relations

## Slide 13
Effectiveness-NTU Relations
TWO LIMITING CASES
For Parallel Flow
For Counter Flow
For Parallel Flow:
For Counter Flow:
For Parallel Flow:
For Counter Flow:

## Slide 14
Effectiveness-NTU Relations
Effectiveness is a function of:
The following observations may be made by reviewing the figures given in the next slides:
  The heat exchanger thermal effectiveness, , increases with the increasing values of NTU for a specified .
  The exchanger thermal effectiveness, , increases with decreasing values of for a specified NTU.
  For <40%, the capacity rate ratio, , does not have a significant influence on the exchanger effectiveness.
The counterflow exchanger has the highest exchanger effectiveness & for specified NTU and C* values compared with those for all other exchanger flow arrangements. Thus, a maximum heat transfer performance is achieved for counterflow compared with all other flow arrangements.

## Slide 15
Effectiveness-NTU Relations

## Slide 16
EXAMPLE-1
A two-pass tube, baffled single-pass shell, shell-and-tube heat exchanger is used as an oil cooler. Cooling water flows through the tubes at 20°C at a flow rate of 4.082 kg/s. Engine oil enters the shell side at a flow rate of 10 kg/s. The inlet and outlet temperatures of oil are 90 and 60°C, respectively. Determine the surface area of the heat exchanger by both the LMTD and ε-NTU methods if the overall heat transfer coefficient based on the outside tube area is 262 W/m2K. The specific heats of water and oil are 4179 J/kg∙K and 2118 J/kg∙K, respectively.
Cooling Water:
Engine Oil:

## Slide 17
EXAMPLE-1-Solution - LMTD
LMTD Method:
Heat capacity rates for shell fluid (oil) and tube fluid (water):
Heat transfer rate from the temperature drop of the oil is:

## Slide 18
EXAMPLE-1-Solution - LMTD
The water outlet temperature from the energy balance is:
Now, let us determine :

## Slide 19
EXAMPLE-1-Solution - LMTD
Now, the values of P and R are:
OR

## Slide 20
One shell pass and two or multiples of two tube passes
EXAMPLE-1-Solution - LMTD

## Slide 21
EXAMPLE-1-Solution - LMTD
Thus, the heat transfer area is:

## Slide 22
EXAMPLE-1-Solution - Ꜫ-NTU
In the ɛ-NTU method, we will firstly calculate and :
In this problem : = and
OR
=

## Slide 23
EXAMPLE-1-Solution - Ꜫ-NTU
From Table 2.2, for 1 to 2 Shell and tube heat exchanger, we have:
NTU
NTU
NTU

## Slide 24
EXAMPLE-1-Solution - Ꜫ-NTU
Hence, the surface area is:

## Slide 30
Heat Exchanger Design Calculations
General Assumptions:
1. The heat exchanger operates under steady-state, steady-flow conditions.
2. Heat transfer to the surroundings is negligible.
3. There is no heat generation in the heat exchanger.
4. In counterflow and parallel-flow heat exchangers, the temperature of each fluid is uniform over every flow cross section; in crossflow heat exchangers each fluid is considered mixed or unmixed at every cross section depending on the specifications.
5. If there is a phase change in one of the fluid streams flowing through the heat exchanger, phase change occurs at a constant temperature for a single-component fluid at constant pressure.
6. The specific heat at constant pressure is constant for each fluid.
7. Longitudinal heat conduction in the fluid and in the wall is negligible.
8. The overall heat transfer coefficient between the fluids is constant throughout the heat exchanger including the case of phase change.
Assumption 5 is an idealization of a two-phase-flow heat exchanger. Especially, for two- phase flows on both sides, many of the foregoing assumptions are not valid. The design theory of these types of heat exchangers is discussed and practical results are presented in the following chapters.

## Slide 31
Heat Exchanger Design Calculations
We have discussed two methods for performing a heat exchanger thermal analysis. The rating and sizing of heat exchangers are two important problems encountered in the thermal analysis of heat exchangers.
For example, if inlet temperatures, one of the fluid outlet temperatures, and mass flow rates are known, then the unknown outlet temperature can be calculated from heat balances and the LMTD method can be used to solve this sizing problem with the following steps:
Calculate Q and the unknown outlet temperature from Equations (2.5) and (2.6).
Calculate from Equation (2.28) and obtain the correction factor F if necessary.
Calculate the overall heat transfer coefficient U.
Determine A from Equation (2.36).
The LMTD method may also be used for rating problems (performance analysis) for an available heat exchanger, but computation would be tedious, requiring iteration because the outlet temperatures are not known.

## Slide 32
Heat Exchanger Design Calculations
In such situations the analysis can be simplified by using the ε-NTU method. The rating analysis with the e-NTU method is as follows:
1. Calculate the capacity rate ratio C*= Cmin/Cmax and NTU = (UA)/Cmin from the input data.
2. Determine the effectiveness, ɛ, from the appropriate charts or ε-NTU equations for the given heat exchanger and specified flow arrangement.
3. When ɛ is known, calculate the total heat transfer rate from Equation (2.43).
4. Calculate the outlet temperatures from Equations (2.5) and (2.6).

## Slide 33
Heat Exchanger Design Calculations
The ε-NTU method may also be used for the sizing problem, and the procedure is as follows:
1. When the outlet and inlet temperatures are known, calculate ɛ from Equation (2.42).
2. Calculate the capacity rate ratio C* = Cmin/Cmax
3. Calculate the overall heat transfer coefficient U.
4. When ε, C*, and the flow arrangement are known, determine NTU from charts or from ε-NTU relations.
5. When NTU is known, calculate the heat transfer surface area A from Equation (2.44).
The use of the ε-NTU method is generally preferred in the design of compact heat exchangers for automotive, aircraft, air-conditioning, and other industrial applications where the inlet temperatures of the hot and cold fluids are specified and the heat transfer rates are to be determined. The LMTD method is traditionally used in the process, power, and petrochemical industries.

## Slide 34
Variable Overall Heat Transfer Coefficient
Let us consider a parallel-flow double-pipe heat exchanger. The heat exchanger is divided into increments of surface area . For any incremental surface area, the hot- and cold-fluid temperatures are and , respectively; and it will be assumed that the overall heat transfer coefficient can be expressed as a function of these temperatures:
The increment heat transfer in can be calculated as:

## Slide 35
Variable Overall Heat Transfer Coefficient
Thus, is also given by:
Must be small enough for the accuracy of the solution
For parallel flow arrangement:
In the finite-difference form:
which can be solved for :

## Slide 36
Variable Overall Heat Transfer Coefficient
The numerical analysis can be conducted as follows:
1. Select a convenient value of for the analysis.
2. Calculate the inner and outer heat transfer coefficients and the value of U for
the inlet conditions and through the initial increment.
3. Calculate the value of ; for this increment from Equation (2.54).
4. Calculate the values of , , and for the next.

## Slide 37
Variable Overall Heat Transfer Coefficient
The total heat transfer rate is then calculated from:
For the overall heat transfer coefficient and varying linearly with , Colburn recommended the following expression to calculate Q: